## Sheet_Office_2
Room Name	Office
Avg maintained illumination for design (Footcandles)	30	see rooms sheet

Luminaire data
Manufacturer
Catalog number

Lamp Data
Type and color
Number per luminaire	1
Total lumens per luminaire	650

Room info
length	12.5
width	9.5
height	8

height of cavities
hCC	1.5
hRC	4	do not edit		5.5	0.8	4.4	1.46666666666667		9.4		2.3
hFC	2.5					7.5

reflectances
r_ceil	80
r_wall_ceil	40	do not edit
r_wall	40
r_wall_floor	40	do not edit
r_floor	20

Cavity Ratios (CR)
Ceiling CR	1.4
Room CR	3.7
Floor CR	2.3

Effective Ceiling Cavity Reflectance	59	80,40,1.4	lookup table 9-11	1.80828272370146
Effective Floor Cavity Reflectance	16	20,40,2.3	lookup table 9-11	0.491144078920499

Coefficient of Utilization	0.84	59,40,3.7	lookup table 9-12

Light Loss Factors
Unrecoverable
Luminarire ambient temp	1
Voltage to luminaire	1
Ballast factor	1
Luminaire surface dep	1

Recoverable
RSDD	1
Lamp lumen depreciation	1
Lamp burnouts factor	1
Luminaire Dirt Depreciations	0.94

LLF	0.94

Num Luminaires	7

Effective Ceiling Cavity Reflectance
A_Ceil	118.75
A_Wall	66
r_ceil	80
r_wall_ceil	40

X = cavity len / cavity depth	8.33333333333333
Y = cavity width / cavity depth	6.33333333333333

F = radiative exchange factor	0.769965047269259	2.56083094023257	0.769965047269259	1.63279232279034	34.3619014598056	48.8891191066048	-8.95656484881492	-12.0947283398047

r_eff_ceil	1.80828272370146		1.80828272370146	3.80835420484415	-11.9787731770274	47.4276939213081

Effective Floor Cavity Reflectance
A_Floor	118.75
A_Wall	110
r_floor	20
r_wall_floor	40

X = cavity len / cavity depth	5
Y = cavity width / cavity depth	3.8

F = radiative exchange factor	0.652501853702957	2.56083094023257	0.652501853702957	1.14761934423292	12.4095073907109	17.7750758101576	-4.99119592493047	-6.86700383472508

r_eff_floor	0.491144078920499		0.491144078920499	5.21441879981305	-1.53881565920311	8.5151733817159

		f23	0.514545029813604

		f21	0.485454970186396
	floor?	f12	0.674715909090909
		f11	0.344911616935972

## Sheet_Office
Room Name	Office
Avg maintained illumination for design (Footcandles)	15	see rooms sheet
length	12.5
width	9.5

lumens per luminaire	800

hCC	1.5
hRC	4
hFC	2.5

r_ceil	80
r_wall_ceil	40	?
r_wall	40
r_wall_floor	40	?
r_floor	25

CCR	1.4
RCR	3.7
FCR	2.3

ECCR	59	80,40,1.4	lookup table 9-11
EFCR	19	25,40,2.3	lookup table 9-11	0.81	0.72

CU	0.36		lookup table 9-12

Light Loss Factors
Unrecoverable
Luminarire ambient temp	1
Voltage to luminaire	1
Ballast factor	1
Luminaire surface dep	1

Recoverable
RSDD	1
LLD	1
LBO	1
LLD	1

LLF	1

Num Luminaires	6

## Sheet_Dining
Room Name	Dining
Avg maintained illumination for design (Footcandles)	15	see rooms sheet

Luminaire data
Manufacturer
Catalog number

Lamp Data
Type and color
Number per luminaire
Total lumens per luminaire	4000

Room info
length	12
width	14.7
height	8
AB	176.5
AW	427.333333333333

height of cavities
hCC	2.5
hRC	3	do not edit
hFC	2.5

reflectances
r_ceil	80
r_wall_ceil	40	do not edit
r_wall	40
r_wall_floor	40	do not edit
r_floor	20

Cavity Ratios (CR)
Ceiling CR	1.9
Room CR	2.3
Floor CR	1.9

Effective Ceiling Cavity Reflectance	52	80,40,1.9	lookup table 9-11
Effective Floor Cavity Reflectance	16	20,40,1.9	lookup table 9-11

Coefficient of Utilization	0.47	52,40,2.3	lookup table 9-12

Light Loss Factors
Unrecoverable
Luminarire ambient temp	1
Voltage to luminaire	1
Ballast factor	1
Luminaire surface dep	1

Recoverable
RSDD	1
Lamp lumen depreciation	1
Lamp burnouts factor	1
Luminaire Dirt Depreciations	0.94

LLF	0.94

Num Luminaires	1

effective_reflectance
AB	176.5
Aw	427.333333333333
r_wall	40
r_base	80

x	4.8
y	5.88333333333332
F	0.703553857700409		1.63731422314396
			1.34039893265475

	25.7841417848591

## rooms
Room Type	Lighting Level	Ft Candles	From Fig. 9-80
Private Office	150,100,70,30	30		+ = equivalent sphere illumination

Residential
Dining	C	15
General	B	7.5		M = general lighting need not be uniform
Kitchen	E, D	75, 30
Bedrooms
Bathroom (grooming)	D	30
Laundry	D	30

	ft candles
A	3
B	7.5
C	15
D	30
E	75
F	150
G	300
H	750
I	1500

## Sheet3
Equivalent sphere p3-20

Es = p3-33

base reflectance	wall reflectance	cavity ratio

			Table 9-11
% ref base	% ref wall	cavity ratio	% eff ref
90	90	0.2	89
		1	86
		2	83
		3	80
		4	77
		5	75
		6	73
		7	70
		8	68
		9	66
		10	65
90	50	0.2	86
		1	75
		2	62
		3	52
		4	44
		5	38
		6	34
		7	30
		8	27
		9	25
		10	22
90	10	0.2	84
		1	64
		2	47
		3	34
		4	25
		5	20
		6	16
		7	14
		8	12
		9	11
		10	9
90	0	0.2	82
		1	62
		2	43
		3	30
		4	22
		5	16
		6	11
		7	8
		8	6
		9	5
		10	4

50	90	0.2	50
		1	50
		2	50
		3	50
		4	50
		5	50
		6	50
		7	49
		8	49
		9	48
		10	47
50	50	0.2	48
		1	43
		2	37
		3	32
		4	28
		5	25
		6	23
		7	21
		8	19
		9	18
		10	17
50	10	0.2	46	41.7635105705636	0.01	17.9478426857264	10.5961306484678
	10	1	36	20.32848298703	1	245.59644548781
	10	2	26	8.26494441107933		314.532196742106
	10	3	19	3.36027563698749		244.600978151007
	10	4	15	1.36618612236463		185.880880850003
	10	5	12	0.555449826912115		130.977728664326
	10	6	10	0.225829047130633		95.5344178159153
	10	7	8	0.091815238851445		62.5393862164622
	10	8	7	0.037329290418834		48.4787834100595
	10	9	7	0.015176956903943		48.7877529433657
	10	10	6	0.006170490204334		35.9259921924974
50	0	0.2	44	40.9365376538991		9.38480154597806
	0	1	34	18.3939720585721		243.548108108628
	0	2	24	6.76676416183064		296.984417453965
	0	3	17	2.4893534183932		210.558864216297
	0	4	12	0.915781944436709		122.859889903275
	0	5	9	0.336897349954273		75.0493475252293
	0	6	6	0.123937608833318		34.5281092248835
	0	7	5	0.045594098277726		24.5461378390205
	0	8	3	0.016773131395126		8.89964254956604
	0	9	3	0.006170490204334		8.96301513372336
	0	10	2	0.002269996488124		3.99092516693156

0	90	0.2	2
		1	8
		2	14
		3	18
		4	22
		5	25
		6	27
		7	28
		8	30
		9	31
		10	31
0	50	0.2	1
		1	4
		2	7
		3	9
		4	10
		5	11
		6	12
		7	12
		8	12
		9	12
		10	12
0	10	0.2	0
	10	1	1
	10	2	1
	10	3	2
	10	4	2
	10	5	2
	10	6	2
	10	7	2
	10	8	2
	10	9	2
	10	10	2
0	0	0.2	0
	0	1	0
	0	2	0
	0	3	0
	0	4	0
	0	5	0
	0	6	0
	0	7	0
	0	8	0
	0	9	0
	0	10	0